|  | ......... pcs .................. € .................. € GEZE THZ Comfort N4 smoke and heat extraction control panel Smoke and heat extraction control panel for the activation of 24 V DC electric linear drives (smoke and heat extraction) or electric hold-open magnets in a vent group or an alarm group. In lockable robust aluminium die-cast surface-mounted casing and integrated smoke and heat extraction as well as ventilation button. Colour: ( ) orange RAL 2011 (VdS statement of approval) Alternatively: ( ) red RAL 3001 ( ) blue RAL 5015 ( ) yellow RAL 1021 ( ) grey RAL 7035 ( ) white RAL 9016 ( ) RAL according to choice Features: Motor control through polarity reversal and automatic battery charger, automatic switchover from mains to battery operation and emergency power supply with rechargeable battery 24 V for at least 72 hours. Connecting of multiple THZ Comfort N4 possible. (Ring or master/slave) Parameter setting and reading out of notifications/operating statuses via GEZE ST 220 service terminal or integrated service keys and service LED. Integrated smoke and heat extraction push button for manual alarm activation with alarm and reset button and LED display for "Fire alarm", "Operation" and "Fault” Clear service interval display via the LED in the control panel Security lighting for better visibility, dimmable. Parameters can be set for integrated vent switch (OPEN/CLOSED) for activation, latching/dead man/deactivated. Possible connections: - Rain/wind control - 10 smoke detectors and/or heat detectors - 8 FT4 A SHEV buttons - Vent switch with or without LED function display (max.3 with LED) - Alarm input for external trigger (fire alarm system), line monitored - Standby current load up to max. 0.8 A e.g. hold-open magnets (note: UPS time is reduced) - Three potential-free status contacts with parameter setting, factory setting: Alarm, fault and window OPEN - Connection for GEZE ST 220 service terminal Technical data: Input voltage: 230 V AC Output voltage: 24 V DC +/- 5 % in mains operation Output voltage:24 V DC +/- 15 % in rechargeable battery operation Residual ripple: 2% Battery capacity: 2.3 Ah, rechargeable battery VdS tested IP rating: IP30 Output current max. 4.5 A; 30 % ED Version: Surface-mounted die-cast casing two-coloured grey and cover colour: Width: 140 mm Height: 248 mm Depth: 85 mm Tested in accordance with DIN EN 60335 and DIN EN 12101-10 VdS statement of approval in accordance with VdS 2581, 2593 |
| --- | --- |
|  | ......................... Stk .............................. € .............................. € GEZE FT4 A/24 V DC SHEV button – VdS for manual alarm triggering with alarm and reset button and LED display for "Fire alarm", "Operation", "Window open" and "Fault", in lockable surface-mounted housing marked "Smoke vent", with break glass pane, die-cast housing in the colour Colour: orange RAL 2011 (VdS approval) Alternatively: ( ) red RAL 3000 ( ) blue RAL 5015 ( ) yellow RAL 1021 ( ) grey RAL 7035 ( ) secondary unit, orange RAL 2011 (only with LED alarm) ( ) acoustic, orange RAL 2011 (with signal in the case of alarm, fault) |
|  | ......... pcs .................. € .................. € GEZE FT4 K/24 V DC SHEV button for manual alarm activation with alarm and reset button and LED display for "Fire alarm", "Operation", "Window open" and "Fault", in lockable surface-mounted casing marked "Smoke extraction", with break glass pane, plastic housing in the colour: Colour: orange similar to RAL 2011 |
|  | ......... pcs .................. € .................. € GEZE smoke detector with base, ( ) RM 1003, EN 54-7 and VdS statement of approval ( ) GC 162 RWA, EN 54-7 permitted for automatic alarm activation in the case of smoke |
|  | ......... pcs .................. € .................. € GEZE heat detector with base, ( ) WM 1005, EN 54-4 and VdS statement of approval ( ) GC 162 RWA, EN 54-4 statement of approval for automatic alarm activation in the case of heat development |
|  | ......... pcs .................. € .................. € GEZE FT 4 A SHEV button for manual alarm triggering with alarm and reset button and LED display for "Fire alarm", "Operation", "Window open" and "Fault", in lockable surface-mounted housing marked "Smoke vent", with break glass pane, die-cast housing in the colour: orange RAL 2011 VdS approved version (G 518004) Alternatively: ( ) red RAL 3000 ( ) blue RAL 5015 ( ) yellow RAL 1021 ( ) grey RAL 7035 |
|  | ......... pcs .................. € .................. € GEZE vent switch for ventilation mode ( ) AS 500 vent switch LTA-24-AZ with control keys “Open-Close” and LED function display, IP rating IP40, to match switch ranges with 55x55mm switch insert, ( ) Surface-mounted ( ) Flush-mounted |
|  | ......... pcs .................. € .................. € GEZE E 70 room temperature regulator for automatic room temperature control. Setting the room temperature from 5 °C to 30 °C and selector switch to change over from manual to automatic operation (1 pc.) |
|  | ......... pcs .................. € .................. € GEZE GC 240 RS rain sensor for the automatic closing of windows in case of rain in ventilation mode, rain sensor (heated electrically) with integrated controller (1 pc.) |
|  | ......... pcs .................. € .................. € GEZE rain/wind control, for the automatic closing of windows in case of rain/wind in ventilation mode, consisting of weather station with rain and wind sensor (heated electrically), controller (1 pc.) |
|  | REMARK: Electrical cable routing and connection on site by an electrical contractor according to the GEZE cable plans. The type of cable to be used is to be determined with the respective local authorities. |
| 1.8 | ......... pcs .................. € .................. € Installation and functional test Installation and functional test by an expert authorised by the manufacturer. |
| 1.9 | ......... pcs .................. € .................. € Start-up and official approval Official approval of the complete smoke and heat extraction system by an officially recognised expert, who also hands over the acceptance certificates. |
| 1.10 | ......... pcs .................. € .................. € Service maintenance - compact package Maintenance and testing of hold-open systems (optional position) Service package for maintenance and testing according to ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - Fault diagnosis and repair jobs during the contract period will be carried out at reduced hourly rates - Service technicians will be deployed within 24 hours of the message being received from Monday – Friday between 7 am and 5 pm without surcharges - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 2 years |
| 1.11 | ......... pcs .................. € .................. € Service maintenance - comfort package Service maintenance (optional position) Comfort service package for maintenance and accident prevention inspection in accordance with ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - Extension of the warranty to 36 months (condition: the maintenance contract is concluded 3 months after the commissioning date at the latest) - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - No separate charging for services and travel costs during the warranty period - No separate charging for consumables up to € 25 per maintenance - No separate charging for working hours when spare parts are replaced during the maintenance - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 3 years |
| 1.12 | ......... pcs .................. € .................. € Delivery and installation Wiring to be carried out on site by an electrical contractor according to the GEZE cable plan. Delivery, installation and commissioning through plant fitters or service partner. Safety analysis, instruction of the operator as to how the system works and handing over of the documentation. Annual maintenance and technical inspection by an expert authorised by the manufacturer incl. documentation of the inspection in an inspection log. |