|  | ......................... pcs. .............................. € .............................. € GEZE spindle drive E 1500 N for a smoke and heat extraction system For daily aeration and ventilation and safe and fast smoke and heat exhaust and smoke extraction on vertically or angled installed, inward and outward opening bottom-hung and top-hung casements as well as for light domes and skylights. Snow and wind loads must be taken into consideration. Electric spindle drive E 1500 N in 24 V version. Built-in end position damping and an integrated electronic overload cut-off must be included in the design. Slide tube and eye must be made of stainless steel. Technical data: Stroke: 300/400/500/750/1000 Tensile force/pressure: 1500 N/1500 N Stroke speed: 4 mm/s** Current consumption: 0.8 A * Enclosure rating: IP 65 Ambient temperature: -5 °C to +75 °C *Design force = maximum force **at 2/3 rated force and 24 V Casement width: ......... mm (max. 1200 mm)1) Casement height: ......... mm 1) For casement widths over 1200 mm, the synchro option must be tendered. Type of window: ( ) Vertically installed bottom-hung, top-hung casements, inward opening ( ) Stroke 300 mm (minimum casement height: 650 mm) ( ) Stroke 400 mm (minimum casement height: 950 mm) ( ) Stroke 500 mm (minimum casement height: 1200 mm) ( ) Vertically installed bottom-hung, top-hung casements, outward opening ( ) Stroke 300 mm (minimum casement height: 400 mm) ( ) Stroke 400 mm (minimum casement height: 400 mm) ( ) Stroke 500 mm (minimum casement height: 400 mm) ( ) Light dome or ( ) Skylight ( ) Stroke 300 m ( ) Stroke 400 mm ( ) Stroke 500 mm ( ) Stroke 750 mm ( ) Stroke 1000 mm ( ) Special stroke ...... mm 2) 2) on request Colour: ( ) EV1 ( ) white RAL 9016 ( ) according to RAL ........ |
| --- | --- |
|  | ......................... pcs. .............................. € .............................. € ( ) Bracket E 1500 ( ) Skylight bracket….......…………(depending on application case) |
|  | ......................... pcs. .............................. € .............................. € ( ) Conical sleeve E 1500 ( ) Casement bracket.....…………(depending on application case) |
|  | ......................... pcs. .............................. € .............................. € Note regarding the tender: You also require an emergency power control unit GEZE E 260 N, MBZ 300, THZ or THZ Comfort and accessories. |
|  | ......................... pcs. .............................. € .............................. € Installation and functional test Installation and functional test by an expert authorised by the manufacturer. |
|  | ......................... pcs. .............................. € .............................. € Start-up and official approval Official approval of the complete smoke and heat extraction system by an officially recognised expert, who also hands over the acceptance certificates. |
|  | ......................... pcs. .............................. € .............................. € Service maintenance - compact package Maintenance and testing of hold-open systems (optional position) Service package for maintenance and testing according to ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - Fault diagnosis and repair jobs during the contract period will be carried out at reduced hourly rates - Service technicians will be deployed within 24 hours of the message being received from Monday – Friday between 7 am and 5 pm without surcharges - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 2 years |
|  | ......................... pcs. .............................. € .............................. € Service maintenance - comfort package Service maintenance (optional position) Comfort service package for maintenance and accident prevention inspection in accordance with ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - Extension of the warranty to 36 months (condition: the maintenance contract is concluded 3 months after the commissioning date at the latest) - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - No separate charging for services and travel costs during the warranty period - No separate charging for consumables up to € 25 per maintenance - No separate charging for working hours when spare parts are replaced during the maintenance - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 3 years |
|  | ......................... pcs. .............................. € .............................. € Delivery and installation Wiring to be carried out on site by an electrical contractor according to the GEZE cable plan. Delivery, installation and commissioning through plant fitters or service partner. Safety analysis, instruction of the operator as to how the system works and handing over of the documentation. Annual maintenance and technical inspection by an expert authorised by the manufacturer incl. documentation of the inspection in an inspection log. |