|  | ......................... pc € .............................. € .............................. GEZE Powerdrive Automatic linear sliding door, for heavy leaf weights TÜV type-tested to DIN 18650, for leaf weights up to 180 kg per leaf (200 kg per leaf with increased opening and hold-open times if appropriate), with self-cleaning rollers for permanently quiet running Drive Drive dimensions (H x D): ( ) 150 x 185 mm or ( ) 200 x 185 mm Integrated battery with charging and monitoring automation for opening or closing in event of power failure Intelligent digital control (category 2 according to DIN EN 954-1 and performance level "d" according to DIN EN ISO 13849-1): - Convenient parameterisation, commissioning and maintenance via optional Bluetooth connection to a PC - Self-learning and with dynamic adjustment of hold-open time in through traffic for optimum convenience - Can be networked and integrated into building systems via CAN bus - Independent error detection and logging - Setting options for all door motion parameters - All functions integrated into a single unit; no other modules required Extremely quiet DC drive Robust power supply with integrated all-pole main switch and fuse protection Static and dynamic power limitation to DIN 18650, plus static under 150 N in accordance with ASR A1.7 (formerly BGR 232) Automatic reversal when an obstacle is detected Dimensions (in unfinished state): Clearance height LH:…………..mm Clearance height LB:............. mm Passage height DH:……….mm Passage width DB:.......... mm ( single leaf 700 - 3000 mm, double leaf 800 - 3000 mm) Installation: ( ) wall mounting or ( ) mounting on profile system or ( ) self-supporting installation Door system version: ( ) single leaf, left-closing ( ) single leaf, right-closing ( ) double leaf ( ) with side elements Fitting: ( ) Moving leaf with ISO or MONO glass, finely framed (up to 120 kg leaf weight): ( ) With 22 mm ISO glass made from ( ) toughened safety glass or ( ) laminated safety glass ( ) With 10 mm ISO glass made from ( ) toughened safety glass or ( ) laminated safety glass ( ) with panel infill or ( ) Sliding leaves with toughened safety glass clamping profile (up to 120 kg leaf weight): ( ) with 10 mm toughened safety glass or ( ) with 12 mm toughened safety glass or ( ) Thermally separated frame moving leaf (up to 200 kg leaf weight) Overall depth 65mm with corresponding special profiles for securing and glazing in accordance with DIN 18650 ( ) With 22 mm ISO glass made from ( ) toughened safety glass or ( ) laminated safety glass ( ) with panel infill Surface of light alloy components of drive and (where applicable) moving leaves: ( ) anodised EV1 or ( ) RAL ........ Electrical wiring to be carried out on site by electrical company in accordance with the GEZE cable plan. Installation, commissioning and operator instruction, plus handing over of documentation in accordance with DIN 18650, to be carried out by installation personnel. Service partner. According to DIN 18650: - the safety analysis must be carried out as a basis for planning and design - testing must be carried out at least once a year and maintenance at least once a year |
| --- | --- |
|  | ......................... pc € .............................. € .............................. Operation GEZE display programme switch in the AS 500 range for setting the mode of operation as well as for putting the drive into operation and setting parameters, with function keys, 2x 7-segment display, alphanumerical fault display, IP rating IP 40 Operating modes: permanently open, automatic, shop closing, night-locking, off ( ) Surface-mounted ( ) Flush-mounted or GEZE button programme switch for setting the mode of operation, with function keys, LED dot display, coded error display, IP 40 enclosure rating, suitable for switch programmes with 55 x 55 mm switch unit Modes of operation: off, permanent hold-open, automatic, closing time, night locking ( ) SM ( ) FM or GEZE mechanical programme switch for setting the mode of operation, with rotary button, LED error display, IP 40 enclosure rating, suitable for switch programmes with 55 x 55 mm switch unit Modes of operation: off, permanent hold-open, automatic, closing time, night locking ( ) SM ( ) FM or GEZE mechanical programme switch for setting the mode of operation, with key, LED error display, IP 40 enclosure rating, suitable for switch programmes with 55 x 55 mm switch unit Modes of operation: off, permanent hold-open, automatic, closing time, night locking ( ) SM ( ) FM |
|  | ......................... pc € .............................. € .............................. Operation (optional item) GEZE key switch for "locking" the programme switch to prevent unauthorised changes to the mode of operation, IP 40 enclosure rating ( ) SM ( ) FM |
|  | ......................... pcs. .............................. € .............................. € Activation and protection (optional position) GC 363+ combined detector with direction detecting radar movement detector for activation and active infrared detector with two light curtains for protection of the opening or closing area in accordance with DIN 18650 / EN 16005, IP54 rating, 10 possible light curtain configurations Version: ( ) black ( ) according to RAL ( ) outside ( ) inside Accessories: ( ) outside: weather hood to protect the sensor from the interference of rain ( ) Ceiling installation bracket ( ) Ceiling installation kit for integrating the sensor in the ceiling (..) Smart Daisy Chain Hub for series connection of up to three sliding door sensors |
|  | ......................... pcs. .............................. € .............................. € Activation and protection (optional position) GC 365 combined detector with direction detecting radar movement detector for activation and active infrared detector with two light curtains for protection of the opening or closing area in accordance with DIN 18650 / EN 16005, IP54 rating, 4 possible light curtain configurations Version: ( ) black ( ) outside ( ) inside Accessories: ( ) outside: weather hood to protect the sensor from the interference of rain ( ) Ceiling installation bracket ( ) Ceiling installation kit for integrating the sensor in the ceiling |
|  | ......................... pcs. .............................. € .............................. € Protection (optional position) GC 339+ active infrared detector with two light curtains for protecting the opening or closing area in accordance with DIN 18650 / EN 16005, IP54 rating, 10 possible light curtain configurations Version: ( ) black ( ) according to RAL ( ) interior ( ) exterior Accessories: ( ) outside: weather hood to protect the sensor from the interference of rain ( ) Ceiling installation bracket ( ) Ceiling installation kit for integrating the active infrared detector in the ceiling (..) Smart Daisy Chain Hub for series connection of up to three sliding door sensors |
|  | ......................... pcs. .............................. € .............................. € Protection (optional position) GC 341 active infrared detector with two light curtains for protecting the opening or closing area according to DIN 18650/EN 16005, IP54 rating, 4 possible light curtain configurations Version: ( ) black ( ) interior ( ) exterior Accessories: ( ) outside: weather hood to protect the sensor from the interference of rain ( ) Ceiling installation bracket ( ) Ceiling installation kit for integrating the active infrared detector in the ceiling |
|  | ......................... pc € .............................. € .............................. Activation (optional item) GEZE radar movement detector with direction sensing and masking of through traffic for control purposes in accordance with DIN 18650, enclosure rating IP 54 ( ) External ( ) Internal |
|  | ......................... pc € .............................. € .............................. Activation (optional position) GEZE elbow switch, plastic, IP rating IP 30 Dimensions: 90 x 180 x 23 mm ( ) white ( ) stainless steel ( ) optional transmitting module ( ) Surface-mounted ( ) Rear panel for attaching the elbow switch to glass (in connection with the transmitting module) or GEZE elbow switch, LS990, IP rating IP 30 Dimensions: 81 x 223 x 51 mm ( ) white ( ) stainless steel ( ) optional transmitting module ( ) Surface-mounted ( ) Flush-mounted or GEZE elbow switch, stainless steel, IP rating IP 65 Dimensions: 72 x 250 x 17 mm ( ) Surface-mounted or GEZE non-contact proximity switch (radar) Plastic with antimicrobial surface, IP rating IP65, multi-colour LED feedback, adjustable acoustic feedback. Additional input to actively change the LED colour. Dimensions: 80 x 80 mm ( ) Flush mounting 12 mm deep ( ) Surface mounting 21 mm deep ( ) Variant for WC or GEZE LED sensor push button, plastic, IP rating IP 69K round, diameter: 100 mm ( ) Flush-mounted ( ) Surface-mounted: mounting ring flat 4 mm ( ) Surface-mounted: mounting ring high 20 mm or GEZE LED sensor push button, glass, IP rating IP 69K round, diameter: 100 mm ( ) Flush-mounted ( ) Surface-mounted: mounting ring flat 4 mm ( ) Surface-mounted: mounting ring high 20 mm or GEZE LED sensor foot switch, glass, IP rating IP69K Dimensions: 100 x 100 x 3 mm ( ) flush-mounting ( ) vertically adjustable installation base for depths of up to 215 mm from the unfinished floor |
|  | ......................... pc € .............................. € .............................. Activation (optional item) GEZE radio programme with secure rolling code encryption for wireless control of the drive (approx. 30m range in the building). Transmitter: ( ) Wireless transmitter with 1 button, IP 54 enclosure rating and wall bracket ( ) Wireless transmitter with 2 buttons, IP 54 enclosure rating and wall bracket ( ) Wireless transmitter with 4 buttons, IP 54 enclosure rating and wall bracket ( ) Wireless transmitter module for optional integration into GEZE elbow switches Receiver: ( ) Wireless receiver module with 2 outputs, 24 V, pulse operation or pulse and continuous operation, for installation in drive or in a concealed casing with IP 20 enclosure rating |
|  | ......................... pc € .............................. € .............................. Activation (optional position) GEZE GCER 300, 1-door SET Access control solution with RFID reader and PIN keypad in stand-alone operation for controlling one door (can be extended to 2 doors). RFID frequency 13.56 MHz. Authorisation is granted through master ID cards in combination with PIN keyboard directly at the reader. Up to 200 persons/ID cards can be authorised. If individual ID cards are lost or become faulty, they can simply be deleted from the system (selective deletion). Two authorisation types for short-time release or continuous release (office function). Configurable door release time. Variable PIN length. Communication between reader and control unit takes place by encrypted data transfer. Functions such as interlocking door system or dementia adjustable. Release buttons can be connected. Set comprising: 1 pc. GEZE GCER 300 I/O Box (ID no. 185707) 1 pc. GEZE GCVR 300 T, RFID reader flush-mounted (ID no. 185708) 2 pc. GEZE GCER 300 system card master (ID no. 185713) 10 pc. GEZE RFID ID card (ID no. 185711) Optional GEZE GCVR Touch 300 T, RFID reader flush-mounted (ID no. 187108) GEZE RFID key fob (ID no. 185712) GEZE GCER AP surface-mounted frame (Id. no. 130024) or GEZE GCER 300 Light, 1-door SET Access control solution with RFID reader and PIN keyboard in stand-alone operation with a relay output for controlling one door located in the secured inner area. RFID frequency 13.56 MHz. Authorisation is granted through master ID cards in combination with PIN keyboard directly at the reader. Up to 200 persons/ID cards can be authorised for short-time release. If individual ID cards are lost or become faulty, they can simply be deleted from the system (selective deletion). Configurable door release time. Variable PIN length. Communication takes place via encrypted data transfer. Set comprising: 1 pc. GEZE GCER 300 Light, RFID reader flush-mounted (ID no. 185710) 1 pc. GEZE GCER 300 system card master (ID no. 185713) 10 pc. GEZE RFID ID card (ID no. 185711) Optional GEZE RFID key fob (ID no. 185712) GEZE GCER AP surface-mounted frame (ID no. 130024) Accessories for GCER 300 / GCER 300 Light Plug-in power supply NT 1.0 A – 24 V DC (optional) Primary: 230 V AC, 50 Hz Secondary: 24 V DC (+/- 5 %) / 1 A (ID no. 130025) Power supply NT 1.1 A – 24 V DC flush-mounted (optional) For installation in deep standard flush-mounted boxes Primary: 230 V AC, 50 Hz Secondary: 24 V DC / 1.1 A (ID no. 151426) Power supply NT 1.5 A – 24 V DC HA (optional) For installation on top hat rails Primary: 230 V AC, 50 Hz Secondary: 21.6 – 26.4 V DC / 1.5 A (ID no. 151425) |
|  | ......................... pc € .............................. € .............................. Activation (optional item) GEZE key switch, external (IP 54 enclosure rating) with or without profile half cylinder and switch function ( ) SM ( ) FM |
|  | ......................... pc € .............................. € .............................. Activation (optional item) GEZE key switch, external (IP 54 enclosure rating) with or without profile half cylinder and engage function for fire service ( ) FM |
|  | ......................... pc € .............................. € .............................. Activation (optional item) GEZE key switch external (IP 54 enclosure rating), designed for use with customer-supplied profile half cylinder from the locking system and 1 pushbutton with a key icon for opening from the inside. The system opens once from locked position when contact is made and locked after the leaf has closed. |
|  | ......................... pc € .............................. € .............................. Activation (optional item) Add-on switch for opening pharmacies |
|  | ......................... pc € .............................. € .............................. Protection (optional item) GEZE protective door leaf for protection to DIN 18650 in front of moving leaf in areas where door presents risk of injury due to severing, crushing or trapping, leaf made from 10 mm toughened safety glass incl. fitting, can be rotated for cleaning purposes May only be used with finely framed moving leaves with ISO glass! ( ) fixing to drive or ( ) fixing to wall Alternative option: ( ) Sensor-based fixed panel protection with 3D light curtain |
|  | ......................... pc € .............................. € .............................. Protection (optional item) GEZE safety leaf for protection to DIN 18650 in areas where door presents risk of injury due to severing or trapping, for post-rail constructions (depending on where the post is located) behind the moving leaf, leaf made from 10 mm toughened safety glass incl. fitting Alternative option: ( ) Sensor-based fixed panel protection with 3D light curtain |
|  | ......................... pc € .............................. € .............................. Protection (optional item) GEZE safety light barrier with 2 transmitters and 2 receivers for securing the opening region, IP 65 enclosure rating. According to DIN 18650, only permissible if a radar movement detector is used on both sides, the power of the door leaves is limited by a power limitation system, and the equipment is not used for people who require a high level of protection! |
|  | ......................... pc € .............................. € .............................. Protection (optional item) GEZE emergency stop switch with glass pane and illumination for switching off the mains voltage, IP 20 enclosure rating An emergency command device (emergency stop switch) is not absolutely necessary according to DIN 18650. ( ) SM ( ) FM |
|  | ......................... pc € .............................. € .............................. Protection (optional item) GEZE emergency stop switch with illuminated mushroom button for emergency opening or emergency unlocking, IP 40 enclosure rating An emergency command device (emergency stop switch) is not absolutely necessary according to DIN 18650. ( ) SM ( ) FM |
|  | ......................... pc € .............................. € .............................. Locking (optional item) ( ) Two-stage electromagnetic locking, integrated in drive, with manual emergency unlocking or ( ) Hook bolt lock (only for fine-framed moving leaf or for thermally separated frame moving leaf) or ( ) Bolt lock for installation on the underside of the door leaf (only for fine-framed moving leaf), prepared for profile cylinder or profile half cylinder ( ) lockable on one side (for 46 mm PHC) or ( ) lockable on both sides (for 71 mm HC) |
|  | ......................... pc € .............................. € .............................. Floor guide (optional item) Continuous floor guide, in anodised aluminium E6/EV1, can be flush-mounted in the floor, guide rail can be removed for cleaning purposes or replaced Recommended for exterior doors with opening widths above 2000 mm |
|  | ......................... pc € .............................. € .............................. Surveillance (optional item) GEZE end position sensor with reed switch certified to VdS class C, for installation in sliding door drive for electronic surveillance of the door leaf (e.g. for external alarm system, building management system, etc.). |
|  | ......................... pc € .............................. € .............................. Service maintenance - compact package Maintenance and testing (option) Service package for maintenance and inspection in accordance with EN 16005, DIN 18650 Part 2 and ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - Fault diagnosis and repair jobs during the contract period will be carried out at reduced hourly rates - Service technicians will be deployed within 24 hours of the message being received from Monday – Friday between 7 am and 5 pm without surcharges - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 2 years e.g. GEZE compact service package |
|  | ......................... pc € .............................. € .............................. Service maintenance - comfort package Service maintenance (optional position) Comfort service package for maintenance in accordance with EN 16005, DIN 18650 Part 2 and ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - Extension of the warranty to 36 months (condition: the maintenance contract is concluded 3 months after the commissioning date at the latest) - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - No separate charging for services and travel costs during the warranty period - No separate charging for consumables up to EUR 25 per maintenance - No separate charging for working hours when spare parts are replaced during the maintenance - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 3 years |
|  | ......................... pc € .............................. € .............................. Service maintenance - exclusive package Service maintenance (optional position) Exclusive service package for servicing, maintenance in accordance with DIN 18650 Part 2 and ASR A1.7 as well as according to manufacturer’s specification with the following performance features: - Extension of the warranty to 60 months (condition: the maintenance contract is concluded 3 months after the commissioning date at the latest) - One maintenance per contract year - Free provision and updating of the test documents - Attachment of the inspection sticker - Complete repair: no separate charging for repairs (parts and working hours) and travel costs during the contract run time - Online access for the client to the project and system data at the contractor’s - Personal availability at the help desk 24 hours a day, 365 days a year - Contract run time: 5 years |